Опросный лист заказа насосного оборудования

Purpose: pump for closed compressor cooling system (circulation)

Quantity: 2 pcs

Pump type: centrifugal

| № | Наименование параметра (характеристики) | Размерность | Требования заказчика |
| --- | --- | --- | --- |
| 1 | ФУНКЦИОНАЛЬНЫЕ |
| 1.1 | Supply | l/min | 50 |
| 1.2 | Pressure | m | 30…40 |
| 1.3 | Inlet/outlet pressure (max.) (g) | kgf/cm2 | Max 4/ Max 4 |
| 1.4 | Cavitation reserve (max.) | m | no |
| 1.5 | For semi-submersible (submersible) pumps: |  |  |
| 1.5.1 | Immersion depth (distance from liquid surface to suction connection) | m | no |
| 2 | PUMPED MEDIUM |
| 2.1 | Name of pumped medium | SUPER A 65 TOSOL |
| 2.2 | Particulate matter content: |
| 2.2.1 | Volume concentration | % |  |
| 2.2.2 | Particle sizes (abrasive/non-abrasive) | mm | 0,25/0,25 |
| 2.3 | Temperature of working medium | 0С | minus 53 to +60 |
| 2.4 | Viscosity (kinematic) | cSt (mm2/s) |  |
| 2.5 | Density | kg/m3 |  |
| 3 | MATERIALS RESISTANT TO THE PUMPED MEDIUM |
|  | To be determined by the manufacturer/supplier |
| 4 | SHAFT SEAL |
| 4.1 | Single/double packing gland seal | Single/double packing gland seal Single/double mechanical seal |
| 4.2 | Single/double mechanical seal |  |
| 5 | OPERATING (INSTALLATION) CONDITIONS |
| 5.1 | Climate version |  | -53…+35 |
| 5.2 | Class of explosion hazard and fire zone of accommodation |  | В-1а |
| 5.3 | Need for cooling/heating medium supply | да/нет | no |
| 6 | ПРИВОД |
| 6.1 | Voltage, number of phases |  | 380 |
| 6.2 | Network frequency |  | 50 |
| 6.3 | Explosion protection version |  | Еxd |
| 6.4 | Rotational speed | any |
| 7 | ДОПОЛНИТЕЛЬНЫЕ ТРЕБОВАНИЯ |
| 7.1 | Spare parts for 2 years The pump shall be supplied with flanges for РN 1.6 MPa, DN determined by the supplier/manufacturer with flange butt (sealing) surface "B" in accordance with Mating flanges, pads and fasteners are not required. The pump unit shall withstand the temperature range of -53...+35 °C when not in operation. |

Характеристики тосола